Tender Descriptive:

- PONZI PSE L -

HERMETIC SLIDING DOOR IN PONZI PSE L LAMINATE

PONZI PSE L SLIDING DOOR WITH HERMETIC SEALING

On the four perimeter sides, equipped with sliding movement in opening and closing and vertical and horizontal

movement of the door in the final closing phase which guarantees perfect air tightness. Made in one door.

The door consists of:

• Fixed wall-covering frame (gaps) perimeter on three sides of the standard 150 mm thick doorway for walls, built in alumium sheet.

•Door compartment cover frame, made of special extruded aluminum alloy profile specially designed for specific use, standard finish anodized natural silver;

•Door thickness mm. 60 built with perimeter frame in special extruded aluminum alloy rounded profiles specially designed for specific use, natural silver anodized standard finish, complete with:

•Self-supporting panel with a complanar sandwich structure made with two sheets of standard colo plastic laminate chosen frm the commercial sammple book ; two 5mm MDF sheets; internal core in high density expaned polystrene, insultating, soundproofing , self- extinguishing and in Class 1 fire resistance; (For doors with a passage greater than

1200 mm, the plastic and / or stainless steel laminate will have vertical junction line, whose position will be univocally and irrevocably determined by the construction constraints of the door panel);

• Perimeter gaskets on all four sides made of EPDM type elastomer;

• Lever pull handle completely in stainless steel for emergency maneuvering;

The sliding and guide mechanism is made with:

• Specially designed and extruded upper track in special aluminum alloy prepared for wall mounting, natural silver anodised finish;

• Two steel carts with large nylon 6.6 wheels mounted on double ball bearings, with height, depth and anti-dum adjustment;

•  Inverted "V" sliding guide made with a special profile in natural silver anodised aluminum, incorporated under the door;

• Composite cover casing, specially designed with rounded antipollution profile and built with AISI 304 stainless steel profiles;

The door in the automatic version includes a specially designed and built automation for sliding doors of the HERMETIC type, complete with:

•  Low voltage electric gear motor with high mechanical reversibility complete with 2-channel optical encoder for position, speed and acceleration detection;

• Microprocessor control board with specific software that automatically manages acceleration, translation, approach and braking according to the weight of the leaves and the surrounding conditions;

• Electronic anti-crushing system both in closing and in opening, with triple control integrated in the control card and complying with the dictates of current regulations;

• Toothed belt transmission system made of neoprene coated in anti-wear and anti-friction material and reinforced with fiberglass / kevlar inserts;

•  Stabilized and filtered 200 W power supply;

•  Supply voltage 230V - 50 Hz - 24 Volt continuous current operation;

•  Control units for opening: n. 2 elbow buttons;

•  Safety sensors for protection in closing: n. 2 active infrared type presence sensors.

N. dimensions da mm……… x mm. H.

Srl

Seat:	48031 BAGNARA (RA)

VIA Gramsci, 26/A Tel. +39 0545 76009

Fax +39 0545 76827

P. IVA 02144680390

20123 MILANO

Viale G. D’Annunzio, 25

Tel. +39 02  8394231

Fax +39 02 89422342

00138 ROMA

Via Salaria, 1378

Tel. +39 06 88566005

Fax +39 0688560406

65015 MONTESILVANO (PE)

Via A. Moro, 6

Tel. +39 085 4483020

Fax. +39 085 4455895

www.ponzi-in.it 	info@ponzi-in.it